## TowerA11004(42)
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119050
Meter Location : 11th FLOOR AHU:-4 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1744.03
1 | Inlet Temp | 12.06 | 53.708
2 | Outlet Temp | 17.67 | 63.806
| Delta T | 5.61 | 10.098 | 21.87 | 96.294 | 486188.406 | 142.5018
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1744.03
1 | Inlet Temp | 13.06 | 55.508
2 | Outlet Temp | 16.75 | 62.15
| Delta T | 3.69 | 6.642 | 15.03 | 66.177 | 219773.817 | 64.4157
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)