## Tower_12THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80589004
Meter Location : 12TH/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1016.63
1 | Inlet Temp | 10.28 | 50.504
2 | Outlet Temp | 13.77 | 56.786
| Delta T | 3.49 | 6.282 | 14.908 | 65.64 | 206175.24 | 60.43
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1016.64
1 | Inlet Temp | 9.62 | 49.316
2 | Outlet Temp | 12.51 | 54.518
| Delta T | 2.89 | 5.202 | 14.06 | 61.906 | 161017.506 | 47.1942
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_12THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119074
Meter Location : 12th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1888.93
1 | Inlet Temp | 8.99 | 48.182
2 | Outlet Temp | 14 | 57.2
| Delta T | 5.01 | 9.018 | 17.61 | 77.537 | 349614.333 | 102.472
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1888.94
1 | Inlet Temp | 9.32 | 48.776
2 | Outlet Temp | 13.51 | 56.318
| Delta T | 4.19 | 7.542 | 17.62 | 77.581 | 292557.951 | 85.7487
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_12THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 85119042
Meter Location : 12th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1494.67
1 | Inlet Temp | 10.46 | 50.828
2 | Outlet Temp | 15.37 | 59.666
| Delta T | 4.91 | 8.838 | 15.06 | 66.309 | 293019.471 | 85.884
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1494.68
1 | Inlet Temp | 9.36 | 48.848
2 | Outlet Temp | 14.47 | 58.046
| Delta T | 5.11 | 9.198 | 15.08 | 66.397 | 305359.803 | 89.501
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_12THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80589074
Meter Location : 12th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1129.36
1 | Inlet Temp | 10.52 | 50.936
2 | Outlet Temp | 13.79 | 56.822
| Delta T | 3.27 | 5.886 | 20.402 | 89.83 | 264369.69 | 77.4868
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1129.37
1 | Inlet Temp | 12.2 | 53.96
2 | Outlet Temp | 13.25 | 55.85
| Delta T | 1.05 | 1.89 | 19.2 | 84.538 | 79888.41 | 23.4153
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_11THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 85119011
Meter Location : 11th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*795.71
1 | Inlet Temp | 10.44 | 50.792
2 | Outlet Temp | 18.02 | 64.436
| Delta T | 7.58 | 13.644 | 15.21 | 66.97 | 456869.34 | 133.9084
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*795.73
1 | Inlet Temp | 10.02 | 50.036
2 | Outlet Temp | 16.12 | 61.016
| Delta T | 6.1 | 10.98 | 15.99 | 70.404 | 386517.96 | 113.2884
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_11THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80599164
Meter Location : 11th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*706.08
1 | Inlet Temp | 9.85 | 49.73
2 | Outlet Temp | 13.94 | 57.092
| Delta T | 4.09 | 7.362 | 15.37 | 67.674 | 249107.994 | 73.0136
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*706.08
1 | Inlet Temp | 10.23 | 50.414
2 | Outlet Temp | 13.56 | 56.408
| Delta T | 3.33 | 5.994 | 15.38 | 67.718 | 202950.846 | 59.4849
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_11THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 84089148
Meter Location : 11th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*886.2
1 | Inlet Temp | 9.68 | 49.424
2 | Outlet Temp | 23.17 | 73.706
| Delta T | 13.49 | 24.282 | 7.237 | 31.865 | 386872.965 | 113.3925
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*886.21
1 | Inlet Temp | 11.31 | 52.358
2 | Outlet Temp | 16.21 | 61.178
| Delta T | 4.9 | 8.82 | 8.21 | 36.149 | 159417.09 | 46.7251
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_11THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119019
Meter Location : 11th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*1255.45
1 | Inlet Temp | 9.99 | 49.982
2 | Outlet Temp | 12.16 | 53.888
| Delta T | 2.17 | 3.906 | 19.63 | 86.431 | 168799.743 | 49.4752
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*1255.47
1 | Inlet Temp | 9.63 | 49.334
2 | Outlet Temp | 12.1 | 53.78
| Delta T | 2.47 | 4.446 | 18.02 | 79.342 | 176377.266 | 51.6962
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_10THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119015
Meter Location : 10th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*589842.29
1 | Inlet Temp | 23.83 | 74.894
2 | Outlet Temp | 24.08 | 75.344
| Delta T | 0.25 | 0.45 | 15.23 | 67.058 | 15088.05 | 4.4223
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*589842.29
1 | Inlet Temp | 22.92 | 73.256
2 | Outlet Temp | 23.02 | 73.436
| Delta T | 0.1 | 0.18 | 14.06 | 61.906 | 5571.54 | 1.633
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_10THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119023
Meter Location : 10th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*956.25
1 | Inlet Temp | 22.92 | 73.256
2 | Outlet Temp | 23.02 | 73.436
| Delta T | 0.1 | 0.18 | 16.63 | 73.222 | 6589.98 | 1.9315
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*956.26
1 | Inlet Temp | 22.01 | 71.618
2 | Outlet Temp | 23.13 | 73.634
| Delta T | 1.12 | 2.016 | 14.06 | 61.906 | 62401.248 | 18.2898
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_9THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119059
Meter Location : 9th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*515.58
1 | Inlet Temp | 8.44 | 47.192
2 | Outlet Temp | 19.48 | 67.064
| Delta T | 11.04 | 19.872 | 14.188 | 62.47 | 620701.92 | 181.9277
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*515.59
1 | Inlet Temp | 9.96 | 49.928
2 | Outlet Temp | 17.02 | 62.636
| Delta T | 7.06 | 12.708 | 14.123 | 62.184 | 395117.136 | 115.8088
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_9THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86229016
Meter Location : 9th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*600.21
1 | Inlet Temp | 8.73 | 47.714
2 | Outlet Temp | 15.95 | 60.71
| Delta T | 7.22 | 12.996 | 4.731 | 20.831 | 135359.838 | 39.674
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*600.22
1 | Inlet Temp | 9.36 | 48.848
2 | Outlet Temp | 15.62 | 60.116
| Delta T | 6.26 | 11.268 | 5.02 | 22.103 | 124528.302 | 36.4992
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_9THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119017
Meter Location : 9th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*832.4
1 | Inlet Temp | 8.66 | 47.588
2 | Outlet Temp | 23.61 | 74.498
| Delta T | 14.95 | 26.91 | 18.47 | 81.323 | 1094200.965 | 320.7103
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*832.42
1 | Inlet Temp | 14.03 | 57.254
2 | Outlet Temp | 19.06 | 66.308
| Delta T | 5.03 | 9.054 | 18.32 | 80.663 | 365161.401 | 107.0288
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_9THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 84089153
Meter Location : 9th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*629.87
1 | Inlet Temp | 8.96 | 48.128
2 | Outlet Temp | 11.51 | 52.718
| Delta T | 2.55 | 4.59 | 20.48 | 90.173 | 206947.035 | 60.6562
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*629.88
1 | Inlet Temp | 9.01 | 48.218
2 | Outlet Temp | 12.63 | 54.734
| Delta T | 3.62 | 6.516 | 19.86 | 87.444 | 284892.552 | 83.502
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_8THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 85119006
Meter Location : 8th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*673.01
1 | Inlet Temp | 14.4 | 57.92
2 | Outlet Temp | 18.77 | 65.786
| Delta T | 4.37 | 7.866 | 14.43 | 63.535 | 249883.155 | 73.2408
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*673.02
1 | Inlet Temp | 13.12 | 55.616
2 | Outlet Temp | 17.05 | 62.69
| Delta T | 3.93 | 7.074 | 14.52 | 63.932 | 226127.484 | 66.278
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_8THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119067
Meter Location : 8th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*543274.09
1 | Inlet Temp | 14.16 | 57.488
2 | Outlet Temp | 23.07 | 73.526
| Delta T | 8.91 | 16.038 | 7.25 | 31.922 | 255982.518 | 75.0285
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*543274.1
1 | Inlet Temp | 10.21 | 50.378
2 | Outlet Temp | 17.23 | 63.014
| Delta T | 7.02 | 12.636 | 7.24 | 31.878 | 201405.204 | 59.0319
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_8THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119071
Meter Location : 8th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*953.36
1 | Inlet Temp | 12.93 | 55.274
2 | Outlet Temp | 16.58 | 61.844
| Delta T | 3.65 | 6.57 | 12.46 | 54.861 | 180218.385 | 52.822
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*953.36
1 | Inlet Temp | 10.06 | 50.108
2 | Outlet Temp | 15.08 | 59.144
| Delta T | 5.02 | 9.036 | 12.44 | 54.773 | 247464.414 | 72.5318
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_8THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119036
Meter Location : 8th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1231.76
1 | Inlet Temp | 12.64 | 54.752
2 | Outlet Temp | 16.23 | 61.214
| Delta T | 3.59 | 6.462 | 15.9 | 70.008 | 226195.848 | 66.298
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1231.78
1 | Inlet Temp | 11.23 | 52.214
2 | Outlet Temp | 17.8 | 64.04
| Delta T | 6.57 | 11.826 | 15.12 | 66.573 | 393646.149 | 115.3777
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_7THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80599038
Meter Location : 7th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*683.42
1 | Inlet Temp | 19.72 | 67.496
2 | Outlet Temp | 20.64 | 69.152
| Delta T | 0.92 | 1.656 | 9.14 | 40.243 | 33321.204 | 9.7664
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*683.44
1 | Inlet Temp | 16.32 | 61.376
2 | Outlet Temp | 18.36 | 65.048
| Delta T | 2.04 | 3.672 | 10.23 | 45.043 | 82698.948 | 24.2391
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_7THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86069001
Meter Location : 7th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*585.98
1 | Inlet Temp | 15.37 | 59.666
2 | Outlet Temp | 17.93 | 64.274
| Delta T | 2.56 | 4.608 | 11.37 | 50.062 | 115342.848 | 33.807
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*585.99
1 | Inlet Temp | 9063 | 16345.4
2 | Outlet Temp | 16.12 | 61.016
| Delta T | -9046.88 | -16284.384 | 11.21 | 49.358 | -401882312.736 | -117791.7059
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_7THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119043
Meter Location : 7th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*949.8
1 | Inlet Temp | 15.2 | 59.36
2 | Outlet Temp | 18.83 | 65.894
| Delta T | 3.63 | 6.534 | 11.89 | 52.352 | 171033.984 | 50.1301
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*949.81
1 | Inlet Temp | 13.2 | 55.76
2 | Outlet Temp | 18.82 | 65.876
| Delta T | 5.62 | 10.116 | 11.88 | 52.308 | 264573.864 | 77.5466
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_7THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119051
Meter Location : 7th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*863.7
1 | Inlet Temp | 14.8 | 58.64
2 | Outlet Temp | 19.45 | 67.01
| Delta T | 4.65 | 8.37 | 7.89 | 34.74 | 145386.9 | 42.6129
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*863.71
1 | Inlet Temp | 13.25 | 55.85
2 | Outlet Temp | 19.46 | 67.028
| Delta T | 6.21 | 11.178 | 8.2 | 36.105 | 201790.845 | 59.1449
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_6THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86229013
Meter Location : 6th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*742.58
1 | Inlet Temp | 11.25 | 52.25
2 | Outlet Temp | 21.16 | 70.088
| Delta T | 9.91 | 17.838 | 10.463 | 46.069 | 410889.411 | 120.4317
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*742.58
1 | Inlet Temp | 12.08 | 53.744
2 | Outlet Temp | 19.26 | 66.668
| Delta T | 7.18 | 12.924 | 11.11 | 48.917 | 316101.654 | 92.6494
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_6THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80599039
Meter Location : 6th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*466.86
1 | Inlet Temp | 11.29 | 52.322
2 | Outlet Temp | 15.2 | 59.36
| Delta T | 3.91 | 7.038 | 14.4 | 63.403 | 223115.157 | 65.3951
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*466.88
1 | Inlet Temp | 10.05 | 50.09
2 | Outlet Temp | 15.36 | 59.648
| Delta T | 5.31 | 9.558 | 14.43 | 63.535 | 303633.765 | 88.9951
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_6THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119021
Meter Location : 6th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*355.89
1 | Inlet Temp | 8.62 | 47.516
2 | Outlet Temp | 8.72 | 47.696
| Delta T | 0.1 | 0.18 | 16.88 | 74.323 | 6689.07 | 1.9606
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*355.9
1 | Inlet Temp | 8.12 | 46.616
2 | Outlet Temp | 9.03 | 48.254
| Delta T | 0.91 | 1.638 | 16.89 | 74.367 | 60906.573 | 17.8517
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_6THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119079
Meter Location : 6th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*587.41
1 | Inlet Temp | 7.68 | 45.824
2 | Outlet Temp | 9.95 | 49.91
| Delta T | 2.27 | 4.086 | 17.06 | 75.115 | 153459.945 | 44.9791
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*587.44
1 | Inlet Temp | 8.23 | 46.814
2 | Outlet Temp | 10.01 | 50.018
| Delta T | 1.78 | 3.204 | 17.04 | 75.027 | 120193.254 | 35.2286
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_5THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119058
Meter Location : 5th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*592.72
1 | Inlet Temp | 22.34 | 72.212
2 | Outlet Temp | 20.51 | 68.918
| Delta T | 1.83 | -3.294 | 10.867 | 47.847 | -78804.009 | -23.0975
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*592.78
1 | Inlet Temp | 12.23 | 54.014
2 | Outlet Temp | 18.21 | 64.778
| Delta T | 5.98 | 10.764 | 10.99 | 48.389 | 260429.598 | 76.3319
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_5THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80599041
Meter Location : 5th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*667.79
1 | Inlet Temp | 18.81 | 65.858
2 | Outlet Temp | 23.8 | 74.84
| Delta T | 4.99 | 8.982 | 8.55 | 37.646 | 169068.186 | 49.5539
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*667.8
1 | Inlet Temp | 15.22 | 59.396
2 | Outlet Temp | 20.32 | 68.576
| Delta T | 5.1 | 9.18 | 8.06 | 35.488 | 162889.92 | 47.743
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_5THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80589083
Meter Location : 5th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*978.7
1 | Inlet Temp | 18.75 | 65.75
2 | Outlet Temp | 18.95 | 66.11
| Delta T | 0.2 | 0.36 | 13.54 | 59.617 | 10731.06 | 3.1453
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*987.7
1 | Inlet Temp | 10.07 | 50.126
2 | Outlet Temp | 16.2 | 61.16
| Delta T | 6.13 | 11.034 | 14.02 | 61.73 | 340564.41 | 99.8194
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_5THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119004
Meter Location : 5th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1016.63
1 | Inlet Temp | 10.28 | 50.504
2 | Outlet Temp | 13.77 | 56.786
| Delta T | 3.49 | 6.282 | 14.908 | 65.64 | 206175.24 | 60.43
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1016.64
1 | Inlet Temp | 9.62 | 49.316
2 | Outlet Temp | 12.51 | 54.518
| Delta T | 2.89 | 5.202 | 14.06 | 61.906 | 161017.506 | 47.1942
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_4THAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80599170
Meter Location : 4th/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*554.67
1 | Inlet Temp | 18.18 | 64.724
2 | Outlet Temp | 19.65 | 67.37
| Delta T | 1.47 | 2.646 | 14.13 | 62.214 | 82309.122 | 24.1248
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*554.68
1 | Inlet Temp | 17.23 | 63.014
2 | Outlet Temp | 19.25 | 66.65
| Delta T | 2.02 | 3.636 | 14.03 | 61.774 | 112305.132 | 32.9166
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_4THAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80589095
Meter Location : 4th/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*500.23
1 | Inlet Temp | 16.23 | 61.214
2 | Outlet Temp | 22.26 | 72.068
| Delta T | 6.03 | 10.854 | 14.92 | 65.693 | 356515.911 | 104.4948
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*500.24
1 | Inlet Temp | 10.01 | 50.018
2 | Outlet Temp | 15.23 | 59.414
| Delta T | 5.22 | 9.396 | 14.01 | 61.686 | 289800.828 | 84.9406
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_4THAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80589081
Meter Location : 4th/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*760.12
1 | Inlet Temp | 13.06 | 55.508
2 | Outlet Temp | 18.76 | 65.768
| Delta T | 5.7 | 10.26 | 23.34 | 102.766 | 527189.58 | 154.5193
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*760.13
1 | Inlet Temp | 11.02 | 51.836
2 | Outlet Temp | 17.03 | 62.654
| Delta T | 6.01 | 10.818 | 19.14 | 84.273 | 455832.657 | 133.6046
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_4THAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80599117
Meter Location : 4th/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-80 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*913.34
1 | Inlet Temp | 18.03 | 64.454
2 | Outlet Temp | 25.39 | 77.702
| Delta T | 7.36 | 13.248 | 18.783 | 82.702 | 547818.048 | 160.5655
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*913.35
1 | Inlet Temp | 14.03 | 57.254
2 | Outlet Temp | 19.52 | 67.136
| Delta T | 5.49 | 9.882 | 18.8 | 82.776 | 408996.216 | 119.8768
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_3RDAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 85119077
Meter Location : 3rd/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*172.45
1 | Inlet Temp | 18.92 | 66.056
2 | Outlet Temp | 19.89 | 67.802
| Delta T | 0.97 | 1.746 | 2.581 | 11.364 | 9920.772 | 2.9078
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*172.46
1 | Inlet Temp | 13.02 | 55.436
2 | Outlet Temp | 16.32 | 61.376
| Delta T | 3.3 | 5.94 | 3.02 | 13.297 | 39492.09 | 11.5751
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_3RDAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 85119060
Meter Location : 3rd/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1122.13
1 | Inlet Temp | 20.59 | 69.062
2 | Outlet Temp | 21.19 | 70.142
| Delta T | 0.6 | 1.08 | 14.639 | 64.456 | 34806.24 | 10.2017
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1122.25
1 | Inlet Temp | 12.06 | 53.708
2 | Outlet Temp | 18.25 | 64.85
| Delta T | 6.19 | 11.142 | 15.01 | 66.089 | 368181.819 | 107.9141
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_3RDAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119049
Meter Location : 3rd/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*961.18
1 | Inlet Temp | 21.01 | 69.818
2 | Outlet Temp | 22.3 | 72.14
| Delta T | 1.29 | 2.322 | 16.123 | 70.99 | 82419.39 | 24.1571
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*961.18
1 | Inlet Temp | 11.31 | 52.358
2 | Outlet Temp | 14.23 | 57.614
| Delta T | 2.92 | 5.256 | 16.23 | 71.461 | 187799.508 | 55.044
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_3RDAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119028
Meter Location : 3rd/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*699.39
1 | Inlet Temp | 20.93 | 69.674
2 | Outlet Temp | 21.65 | 70.97
| Delta T | 0.72 | 1.296 | 10.949 | 48.208 | 31238.784 | 9.1561
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*699.41
1 | Inlet Temp | 13.26 | 55.868
2 | Outlet Temp | 17.52 | 63.536
| Delta T | 4.26 | 7.668 | 12.02 | 52.924 | 202910.616 | 59.4731
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_2NDAHU1
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 80589115
Meter Location : 2nd/AHU1 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*593.85
1 | Inlet Temp | 17.48 | 63.464
2 | Outlet Temp | 20.13 | 68.234
| Delta T | 2.65 | 4.77 | 20.22 | 89.029 | 212334.165 | 62.2351
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*593.86
1 | Inlet Temp | 16.3 | 61.34
2 | Outlet Temp | 18.21 | 64.778
| Delta T | 1.91 | 3.438 | 19.26 | 84.802 | 145774.638 | 42.7265
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_2NDAHU4
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 95269054
Meter Location : 2nd/AHU4 | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*480.62
1 | Inlet Temp | 18.95 | 66.11
2 | Outlet Temp | 19 | 66.2
| Delta T | 0.05 | 0.09 | 20.13 | 88.632 | 3988.44 | 1.169
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*480.62
1 | Inlet Temp | 14.01 | 57.218
2 | Outlet Temp | 16.09 | 60.962
| Delta T | 2.08 | 3.744 | 17.13 | 75.423 | 141191.856 | 41.3833
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_2NDAHU2
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 81109062
Meter Location : 2nd/AHU2 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*753.81
1 | Inlet Temp | 18.1 | 64.58
2 | Outlet Temp | 19.89 | 67.802
| Delta T | 1.79 | 3.222 | 16.25 | 71.549 | 115265.439 | 33.7843
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*753.82
1 | Inlet Temp | 12.13 | 53.834
2 | Outlet Temp | 15.06 | 59.108
| Delta T | 2.93 | 5.274 | 19.04 | 83.833 | 221067.621 | 64.7949
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_2NDAHU3
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 98079005
Meter Location : 2nd/AHU3 | [5 empty] | Location : Cyber Park
Meter Size : DN-65 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*864568.34
1 | Inlet Temp | 20.57 | 69.026
2 | Outlet Temp | 21.44 | 70.592
| Delta T | 0.87 | 1.566 | 19.24 | 84.714 | 66331.062 | 19.4416
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*864568.35
1 | Inlet Temp | 11.41 | 52.538
2 | Outlet Temp | 16.01 | 60.818
| Delta T | 4.6 | 8.28 | 19.01 | 83.701 | 346522.14 | 101.5656
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_1STAHU1VOLVO
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 9289017
Meter Location : 1st/AHU1(VOLVO) | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*348919.6
1 | Inlet Temp | 13.84 | 56.912
2 | Outlet Temp | 14.06 | 57.308
| Delta T | 0.22 | 0.396 | 5.285 | 23.27 | 4607.46 | 1.3504
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | KWH= BTU*348919.61
1 | Inlet Temp | 12.24 | 54.032
2 | Outlet Temp | 14.06 | 57.308
| Delta T | 1.82 | 3.276 | 6.21 | 27.343 | 44787.834 | 13.1273
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)

## Tower_1STAHU2ATRIUM
Registered Office: 612, Swastik Disa Corporate Park, LBS Road, Ghatkopar (West), Mumbai Maharashtra -400086
BTU Meter Calibration Report
Serial No: 86119062
Meter Location : 1st/AHU2(Atrium) | [5 empty] | Location : Cyber Park
Meter Size : DN-50 | [6 empty] | Model No : tprime-280 T
Before Calibration(100% Valve Open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1626.05
1 | Inlet Temp | 10.82 | 51.476
2 | Outlet Temp | 16.49 | 61.682
| Delta T | 5.67 | 10.206 | 19.623 | 86.4 | 440899.2 | 129.2276
After Calibration(100% Valve open)
|  | Degree Cel | Fahrenheit | M3/Hr | GPM | BTU= GPM x DeltaT x 500 | MWH= BTU*1626.07
1 | Inlet Temp | 10.12 | 50.216
2 | Outlet Temp | 16.06 | 60.908
| Delta T | 5.94 | 10.692 | 18.02 | 79.342 | 424162.332 | 124.322
Remark:- METER CALIBRATED SUCESSFULY
Completed By
(MANISH GAUTAM)